## Sheet1
Data Center Location | Active Rectifier Cap. | Redundant Rectifer Cap. | Active Rectifier Load | Redundant Rectifier Load | Total DC load | Active Rectifer Battery Charging load | Redundant Rectifier Battery Charging load | Total Battery Charging load | Rectifer Usage (%) | Active UPS Cap. | Redundant UPS Cap. | Active UPS Load | Redundant UPS Load | Total UPS load | Active UPS Battery charging load | Redundant UPS Battery Charging Load | Total UPS Battery Charging load | UPS Usage (%) | Cooling load | Total Installed Capacity | Running Capacity | Sanction load | Active DG Cap. | Redundant DG Cap. | DG Load on Running Cap. | Battery Backup hrs. | PUE
Uttara DC | 120 | 120 | 16 | 21 | 37 | 7.5 | 7.5 | 15 | 37.08% | 32 | 32 | 2.5 | 2.5 | 5 | 3.5 | 3.5 | 7 | 26.56% | 46.5 | 128.5 | 87 | 120 | 120 | 200 | 87 | 2.7243 | 2.0714 | 72.5%
Kawranbazar DC | 72 | 72 | 14 | 14 | 28 | 20 | 20 | 40 | 66.67% | 32 | 32 | 4 | 4 | 8 | 4.8 | 4.8 | 9.6 | 40% | 40.8 | 144.4 | 91 | 200 | 160 | 320 | 91 | 2.7429 | 2.5278
Paltan DC | 120 | 120 | 28.4 | 22 | 50.4 | 12 | 12 | 24 | 52% | 50 | 50 | 8 | 8 | 16 | 9.6 | 9.6 | 19.2 | 51.2% | 53 | 180.6 | 210 | 200 | 400 | 400 | 209 | 0.91429 | 3.1627
Paltan_1 | 72 | 72 | 21.65 | 23.3 | 44.95 | 10 | 10 | 20 | 76.32% | [10 empty] | 82.95 |  |  | N/A | N/A |  | 0.96107
Kaliakoir DC | 72 | 72 | 6.25 | 6.25 | 12.5 | 7.5 | 7.5 | 15 | 27.78% | 48 | 48 | 10 | 10 | 20 | 4.08 | 4.08 | 8.16 | 50.17% | 26.4 | 100.06 | 62 | 100 | 200 | 80 | 76 | 4.608 | 1.9077
Dhanmondi DC | 24 | 22 | 4.1 | 1.85 | 5.95 | 4 | 4 | 8 | 45.23% | 16 | 16 | 3 | 3 | 6 | 7.68 | 7.68 | 15.36 | 85.5% | 12.6 | 65.91 | 30 | 50 | 48 | N/A | 28 | 2.5815 | 2.5105
Bogura DC | 120 | 120 | 15.8 | 11.7 | 27.5 | 7.5 | 7.5 | 15 | 29.17% | 8 | 8 | 1 | 1 | 2 | 3.84 | 3.84 | 7.68 | 73% | 18 | 88.18 | 68 | 100 | 80 | 80 | 72 | 1.8327 | 2.3051
CTG_South | 120 | 120 | 11.65 | 12.6 | 24.25 | 7.5 | 7.5 | 15 | 26.46% | 16 | 16 | 2.5 | 2.5 | 5 | 3.84 | 3.84 | 7.68 | 55.25% | 18 | 87.93 | 62 | 180 | 200 | N/A | 76 | 2.0784 | 2.1197
CTG_North | 72 | 72 | 9.95 | 10.1 | 20.05 | 7.5 | 7.5 | 15 | 38.26% | 4.8 | 4.8 | 1 | 1 | 2 | N/A | N/A | 0 | 0% | 19.8 | 74.85 | 50 | 45 | 80 | N/A | 62 | 2.5137 | 2.2676
Jashore DC | 120 | 120 | 19.25 | 16.75 | 36 | 15 | 15 | 30 | 42.5% | 4.8 | 4.8 | 0.8 | 0.8 | 1.6 | N/A | N/A | 0 | 0% | 26.4 | 112 | 90 | 250 | N/A | N/A | 90 | 2.8 | 2.3936
Benapole DC | 24 | 24 | 7.95 | 6.25 | 14.2 | 7.5 | 7.5 | 15 | 90.42% | 4.8 | 4.8 | 0.8 | 0.8 | 1.6 | N/A | N/A | 0 | 0% | 9.6 | 58.4 | 42 | 47 | 120 | 80 | 42 | 3.5493 | 2.6582
Benapole_2 | 24 | 24 | 1.75 | 2.2 | 3.95 | 2 | 2 | 4 | 24.79% | [5 empty] | N/A | N/A | 0 | 0% | 0 | 25.95 |  |  | N/A | N/A |  | 0.97215
Sylhet DC | 72 | 72 | 8.25 | 8.6 | 16.85 | 10 | 10 | 20 | 37.29% | 8 | 8 | 2.5 | 2.5 | 5 | 2.4 | 2.4 | 4.8 | 92.5% | 31 | 95.65 | 65 | 84 | 80 | N/A | 65 | 2.7347 | 2.9748
Mymensingh DC | 24 | 24 | 4.2 | 4.5 | 8.7 | 5 | 5 | 10 | 57.08% | 8 | 8 | 1 | 1 | 2 | 2.4 | 2.4 | 4.8 | 55% | 10.8 | 54.3 | 24 | 40 | 80 | N/A | 24 | 2.2069 | 2.243